## Slide 1: Title Slide
Pixel Inner System
Cooling
Rafael Coelho Lopes de Sa
Anirudh J. Uppal
US-ATLAS ITk Pixel Inner System Meeting
Apr 27th 2020

## Slide 2: Summary of cooling strategy
warm nose
Boundary conditions
capillary
exhaust
evaporator
flex (??)
(x2)
Q1
Q2
Q3
Q4
Q4 has the PixLumi and BCM’ rings which are not counted here (because I have no idea how much power they use)

## Slide 3: Barrel L0
Using and exhaust tube with ID = 3mm. Evaporator with ID = 2.3mm. Capillary with 2.7m
Should fit well in the tray.
Heat dissipation to most recent recommendations [FE (0.8)+ sensor (0.041)+ services (0.092)]
Result: capillary ID = 0.820mm

## Slide 4: Barrel L1
Using and exhaust tube with ID = 3mm. Evaporator with ID = 3mm. Capillary with 2.7m
Heat dissipation to most recent recommendations [FE (0.8) + sensor (0.013) + services (0.077)]
Result: capillary ID = 1.325mm

## Slide 5: Endcap R0/1
Design fixes the length of capillary (currently 72cm). This may be problematic, since is very large and it may be difficult, in practice, to reach the design .
Evaporator ID=2.3mm
Capillary ID=0.685mm

## Slide 6: Endcap R0/1
Design fixes the length of capillary (currently 72cm). This may be problematic, since is very large and it may be difficult, in practice, to reach the design .
Evaporator ID=2.3mm
Capillary ID=0.685mm

## Slide 7: Endcap R1
Design fixes the length of capillary (currently 72cm). This may be problematic, since is very large and it may be difficult, in practice, to reach the design .
Evaporator ID=2.3mm
Capillary ID=0.635mm

## Slide 8: Endcap R0.5
Again, length of capillary fixed by design (72cm). It would be good to have some room for design.
The coolant mass flow is very different. For instance 1.1g/s here against 3.6g/s in the R0/1. This is also not ideal for manifolding.
Evaporator of ID=2.3mm does not work. Too big, creates unstable flow. Here we use evaporator ID=1.5mm and calculate a capillary with ID=0.443mm

## Slide 9: L0 simulation at smaller radius
Quick check of L0 condition at smaller radius (R=34mm)
Updated bias voltage and heat dissipation for 3D sensor at fluence of 1e16 neq/cm2 (design fluence is 1.86e16 neq/cm2, so this is slightly “optimistic” compared to end-of-life)
This is very preliminary. A complete re-run of the FEA is being performed. But I was asked to provide some partial feedback.
Pessimistic HTC
Pessimistic glue coverage
Pessimistic foam thermal conductivity

## Slide 10: Some quick plots
Again, I change HTC but do not iterate with thermo-fluidic simulation (yet)
L0 stave, as before, is very far away from runaway.
If (max) current has to be kept below 10nA, we need T < -23oC
For FE temp below -10oC, we need T < -19oC.
Chart: Max Pixel Current
| -35 | -33 | -31 | -29 | -27 | -25 | -23 | -21 | -19 | -17 | -15 | -13 | -11 | -10 | -9 | -8
 | 2.0379 | 2.6624 | 3.3732 | 4.3327 | 5.617 | 7.0787 | 9.0097 | 11.6546 | 15.0634 | 19.462 | 25.4665 | 33.8467 | 46.2241 | 55.6003 | 66.0333 | 82.6692
Chart: Max Sensor Temp
| -35 | -33 | -31 | -29 | -27 | -25 | -23 | -21 | -19 | -17 | -15 | -13 | -11 | -10 | -9 | -8
 | -26.9852 | -24.9479 | -22.9058 | -20.8562 | -18.7904 | -16.7153 | -14.6198 | -12.5021 | -10.2679 | -7.8732 | -5.3697 | -2.694 | 0.30302 | 1.995 | 3.8149 | 6.0595
Chart: Max FE Temp
| -35 | -33 | -31 | -29 | -27 | -25 | -23 | -21 | -19 | -17 | -15 | -13 | -11 | -10 | -9 | -8
 | -26.9502 | -24.913 | -22.871 | -20.8216 | -18.7561 | -16.6815 | -14.5865 | -12.4696 | -10.2681 | -7.8735 | -5.3702 | -2.6947 | 0.302 | 1.9937 | 3.8134 | 6.0576

## Slide 11: It looks ok…
But this is very preliminary, take with grain of salt.
A complete study will be ready soon.
Chart: Max Pixel Current
| -35 | -33 | -31 | -29 | -27 | -25 | -23 | -21 | -19 | -17 | -15 | -13 | -11 | -10 | -9 | -8
 | 2.0379 | 2.6624 | 3.3732 | 4.3327 | 5.617 | 7.0787 | 9.0097 | 11.6546 | 15.0634 | 19.462 | 25.4665 | 33.8467 | 46.2241 | 55.6003 | 66.0333 | 82.6692